## Slide 1: S&P USA & the 2012 International Residential and Mechanical Code for Ventilation

## Slide 2: S&P and IRC/IMC 2012
To understand sections of IRC concerning ventilation
To understand sections of IMC concerning ventilation
Identify S&P compliance options
Presentation Objectives

## Slide 3: Chapter 15: The code in regards to ventilation
Section 1

## Slide 4: IRC 2012: Chapter 15
Clothes Dryer Exhaust (M1502)
Range Hood Exhaust (M1503)
Mechanical Ventilation (M1507)
  Whole-house Ventilation
  Local Exhaust
Sections Requiring Ventilation

## Slide 5: Section M1502: Clothes Dryer Exhaust
The dryer exhaust MUST terminate to the outside
The MAX. length of the [dryer] exhaust duct is 35’ from the connection to the outlet terminal
The Code Specifies:
Section 1502 M1502
What if the dryer is NOT located close to the outlet terminal?
What if the duct is longer than 35’ so elbows are necessary creating complicated duct work? (ref. table 1502.4.4.1)
FACT: When ducting from a dryer to the outlet is long and/or complicated the dryer cannot overcome the static pressure thus reducing efficiency and causing increased or poor drying time.
Problem Created by Code:
A Clothes Dryer Booster Fan will help overcome the static pressure created from long and/or complicated duct runs.
S&P’s Solution:

## Slide 6: S&P Solution for M1502
Centrifugal blade design capable of overcoming extreme resistance (high static pressure)
Class F insulation
“Fail-safe” activation method with Current Sensor
Fan only runs when device senses current
PV100X with Current Sensor
Section M1502 Clothes Dryer Exhaust

## Slide 7: Section M1503: Range Hoods
Makeup air is required when system is capable of exhausting 400+ CFM
  Rate of makeup air must be (approx.) equal to the exhaust air
The Code Specifies:
Section M1503 Range Hoods
Simple...Makeup Air!
Why You Need S&P:
GOOD: TD-MIXVENT (Mixed Flow Fan)
BEST: TD-SILENT (Mixed Flow Fan)
S&P’s Solutions:

## Slide 8: Good Solution for Makeup Air
TD-200 with filter box & backdraft damper
  Meets the requirement
  Prevents cold air from infiltrating
  Filters the incoming air
  Distributes air through a small round grille
  Brings air in through an aluminum outdoor grille
TD MIXVENT: Mixed Flow Fan
Section M1503 Range Hoods
  The TD-200 operates at 2 sones! That’s just twice as loud as a refrigerator.

## Slide 9: Better Solution for Makeup Air
TD-200S w/filter box & backdraft damper
  Meets the requirement
  Prevents cold air from infiltrating
  Filters the incoming air
  Distributes air through a small round grille
  Brings air in through an aluminum outdoor grille
TD SILENT: Extremely Quiet Mixed Flow Fan
Section M1503 Range Hoods
  The TD-200S Silent operates at .5 sones! That’s ½ as quiet as a refrigerator.

## Slide 10: Section M1507: Mechanical Ventilation
Whole-house Ventilation AND Local Exhaust is required
Bathroom & toilet air must be exhausted directly to the outdoors and shall not be recirculated within residence
The Code Specifies:
Section M1507 Mechanical Ventilation
One or more supply or exhaust fans, plus associated ducts and controls
Local exhaust or supply fans contribute to the whole-house ventilation requirement
System must have controls that enable manual override
Outdoor (makeup) air must be provided at a continuous rate (ref. Table 1507.3.3)
  Exception: if you use controls that enable operation for at least 25% of each 4 hour segment you can operate intermittently
Whole-house Ventilation Requirements
Section M1507 uses the ASHRAE 62.2 Standards
We will start with the Whole-house Ventilation Requirements

## Slide 11: Whole House Ventilation
Table 1507.3.3: The amount of whole house ventilation that is required to meet the standard.
DWELLING UNIT FLOOR AREA (square feet) | NUMBER OF BEDROOMS |  |  |  | 
 | 0-1 | 2 -3 | 4 -5 | 6-7 | > 7
 | Airflow in CFM |  |  |  | 
< 1,500 | 30 | 45 | 60 | 75 | 90
1,501-3,000 | 45 | 60 | 75 | 90 | 105
3,001-4,500 | 60 | 75 | 90 | 105 | 120
4,501-6,000 | 75 | 90 | 105 | 120 | 135
6,001-7,500 | 90 | 105 | 120 | 135 | 150
> 7,500 | 105 | 120 | 135 | 150 | 165
For SI: 1 square foot = 0.0929 m2, 1 cubic foot per minute = 0.0004719 m3/s.
Section M1507 Mechanical Ventilation

## Slide 12: Good Solution: Whole House Ventilation
  The PC Fan will run continuously for exhaust
  The TD will provide outdoor air continuously
  A speed control should be used to set the TD to match the PC performance
  You meet the code but don’t exceed it!
Section M1507 Mechanical Ventilation
PC-Premium CHIOCE Fan (Exhaust)
TD-MIXVENT Fan (Supply)

## Slide 13: Exhaust Side of Good Solution
Install PC fan in hallway or other area away from the living space
Motors rated for 30,000 hours continuous on
The extremely low sound levels ensure the PC will not be intrusive
ENERGY STAR® qualification ensures the fan reduces energy consumption without sacrificing performance
Section M1507 Mechanical Ventilation
PC Bonus Feature:
Simple Plug-&-Play Speed Control
PCSC option allows you to set the continuous speed requirement. No separate wall control needed!

## Slide 14: Supply Side of the Good Solution
Insert TD Fan into the outside air duct
Set the performance for the whole house requirement and the exhaust requirement totaling the makeup air
Section M1507 Mechanical Ventilation

## Slide 15: Better Solution for Whole House Ventilation
Exhaust Fan set at the required airflow for installed in hallway
Supply Fan in the outside air duct set at the requirement for Kitchen Ventilation, Bathroom Ventilation, & Whole House ventilation.
TD-SILENT: REQUIRES 2 FANS
Section M1507 Mechanical Ventilation

## Slide 16: Best Solution for Whole House Ventilation
Use ERV or HRV to bring in the outside air AND exhaust the air to meet the requirement
With S&P TR or HR the exhaust and supply air do not mix in the core
No need to worry about bathroom air cross contamination so it meets the code (see following sides for airflow animation)
TR: Energy Recovery Ventilator OR
HR: Heat Recovery Ventilator
Section M1507 Mechanical Ventilation

## Slide 20
z

## Slide 22: Section M1507: Mechanical Ventilation
Section M1507 Mechanical Ventilation
Exception: The whole-house mechanical ventilation system is permitted to operate intermittently where the system has controls that enable operation for not less than 25-percent of each 4-hour segment and the ventilation rate prescribed in Table M1507.3.3(1) is multiplied by the factor determined in accordance with Table M1507.3.3(2).
Whole-house Ventilation Requirements EXCEPTION

## Slide 23: Section M1507: Mechanical Ventilation
Section M1507 Mechanical Ventilation
Outdoor (makeup) air must be provided at a continuous rate (ref. Table 1507.3.3)
  Exception: if you use controls that enable operation for at least 25% of each 4 hour segment you can operate intermittently.
  Use Chart 1503.3.3 to determine intermittent factor (Whole House Required CFM x Factor = Intermittent CFM):
EXCEPTION: Whole-house Ventilation Specifies:
RUN-TIME PERCENTAGE IN EACH 4-HOUR SEGMENT | 25% | 33% | 50% | 66% | 75% | 100%
Factor | 4 | 3 | 2 | 1.5 | 1.3 | 1.0
Exception Example: 2000 sq. ft. Home with 2 Baths
  Whole House Requirement = 60 CFM continuous
  Exception: Use a timer to run fan 25% of the four hour period
  The intermittent CFM requirement would be 240 CFM to operate at 25%

## Slide 24: Section M1507: Mechanical Ventilation
Whole-house Ventilation AND Local Exhaust is required
Bathroom & toilet air must be exhausted directly to the outdoors and shall not be recirculated within residence
The Code Specifies:
Section M1507 Mechanical Ventilation
Exhaust the minimum air flow rate based on Table M1507.4
Local Exhaust Ventilation Requirements
AREA TO BE EXHAUSTED | EXHAUST RATES
Kitchens | 100 cfm intermittent or 25 cfm continuous
Bathrooms-Toilet Rooms | Mechanical exhaust capacity of 50 cfm intermittent or 20 cfm continuous
S&P’s Recommended Solutions for Local Exhaust
  GOOD: PC-Premium CHOICE Ventilation Fan (Ceiling Mounted Fan) BETTER: TD-MIXVENT (Mixed Flow Fan)
  BEST: TR or HR (ERV or HRV)

## Slide 25: IMC Sections: The code in regards to ventilation
Section 2

## Slide 26: IMC 2012: Ventilation Sections
Ventilation System (403.1)
Outdoor Air Required (403.2)
Min Air Flow Rates (403.3)
Exhaust Ventilation (403.4)
Variable Air Volume system control (403.6)
Balancing (403.7)
Sections Requiring Ventilation
2012 Code Applies to Multi-Family Projects

## Slide 27: Section 403.1, 403.2, 403.4
Supply and Return (Exhaust) Air is required
Supply Air must equal mount of Exhaust Air
403.1 (Ventilation System) - The Code Specifies:
Section 1502 M1502
Minimum airflow rate determined by Section 403.3
Must deliver required rate of outdoor airflow to the BREATING ZONE within each OCCUPIABLE SPACE
403.2 (Outdoor Air Required) – The Code Specifies
All IRC 2012 Residential Solutions can be used as IMC 2012 Commercial Solutions!
Exhaust airflow rate determined by Section 403.3
Exhaust makeup air can be combination of outdoor air, recirculated air and transfer (except as limited by Section 403.2)
403.4 (Exhaust Ventilation) – The Code Specifies

## Slide 28: Section 403.3 Minimum Air Flow Rates
BREATHING ZONES
OCCUPIABLE SPACE
Exhaust Airflow Rate

## Slide 29: Section 404.6 Variable Air Volume System Control
Controls required to regulate the flow of outdoor air
Control system must be designed to maintain the outdoor airflow rate required by Section 403.3
The Code Specifies:
Section 1502 M1502
CVC – Continuous Ventilation Controls
  Designed exclusively for TD-100, TD-100x and TD-150 to allow the fans to run continuously at a low rate
Percentage Timers
  Multiple options based on fan chosen!
S&P Solutions for Controls
TR Specific
HR Specific
General Options

## Slide 30: Conclusions
Supply Air is just as important as Exhaust Air
S&P offers a number of efficient and cost effective solutions to the IRC 2012 Chapter 15 Requirements
All the products we discussed in the residential section translate into commercial.
What we have learned
TR & HR (ERVs & HRVs)
TD-MIXVENT and TD-SILENT
PC-Premium CHOICE Fans
S&P Exhaust & Supply Options

## Slide 31: Thank you! Any Questions?